## Wants & Needs
FactoryTalk View / FactoryTalk SE Suite → Ignition Migration
Wants & Needs Tracker — fill in the yellow-highlighted columns for each requirement
ID | Category | Item / Requirement | Priority | Description / Rationale | Current State (FactoryTalk) | Target State (Ignition) | Status | Owner | Notes
1 | Licensing | Unlimited tag/client licensing model | Need | Avoid per-tag and per-client licensing overruns as the site scales. | Per-client, activation-based licensing model currently in use. | Server-based licensing with unlimited client connections. | Not Started | FBCO | Confirm license tier and total tag count with Ignition integrator before purchase.
2 | Screens/HMI | Recreate all operator graphics with optimization | Need | All existing FactoryTalk View SE displays must have Ignition equivalents completed prior to cutover, with optimization opportunities considered where practical. | FactoryTalk View SE displays currently in use throughout the facility. | Perspective and/or Vision screens developed in Ignition. | Not Started | FBCO & One Shot | Establish a screen template/navigation standard before recreating individual displays.
3 | Alarming | Migrate alarm configuration and history | Need | Preserve alarm setpoints, priorities, and historical alarm log for compliance purposes. | FactoryTalk Alarms and Events module. | Ignition Alarming module. | Not Started | FBCO & One Shot | Coordinate with alarm rationalization effort (see ID 30) to avoid duplicate work.
4 | Historian | Historical data strategy (retention, migration, and going-forward historian) | Want | Retain historical process data for a specified retention period to support reporting and trending, and determine whether existing FactoryTalk Historian data should be migrated into Ignition or archived separately for compliance retention. | FactoryTalk Historian SE; migration path for existing historical data not yet determined. | Ignition Tag Historian module for going-forward data, with existing historical data either migrated into Ignition or archived per a documented retention plan. | Pending Input | FBCO & One Shot | Confirm PSM/regulatory retention requirements before deciding archive vs. migrate.
6 | Reporting | Shift/production reports | Want | Recreate existing shift reports with the same key performance indicators (KPIs). | No shift/production reports currently exist. | Ignition Reporting module. | Not Started | FBCO & One Shot | Collect existing report templates and KPIs from operators before rebuilding.
7 | Security | Role-based, multi-user access control, including mobile/remote access | Need | Replace the current single shared login with multi-user access and role-based permission levels for operators, engineers, and administrators, and extend remote access capability based on user permission level. | Only one shared user login is currently in use, with a single general permission level granting full control and full access regardless of role; remote access availability is limited. | Ignition Identity Provider with Active Directory (AD) integration, supporting multiple named users with role-based function limitations, including Perspective mobile and web-based access scoped to each user's role. | Not Started | FBCO & One Shot | Confirm VPN/network requirements for remote access before scoping.
9 | Training | Operator/engineer training plan, sandbox, and cutover/rollback plan | Need | Staff must be proficient in the new system prior to go-live. Determine the need for a practice/training environment prior to go-live, and define whether cutover will be a hard switch or a parallel run with rollback capability. | No formal training curriculum, sandbox environment, or cutover/rollback plan currently defined. | Ignition training (including Inductive University coursework) delivered via a practice/training sandbox environment prior to go-live, paired with a documented cutover plan (parallel run or hard cutover) and rollback procedure. | Pending Input | FBCO | Schedule training close to go-live to maximize retention. Gauge operator comfort level with hard cutover vs. running both systems briefly.
10 | Integration | PLC/controller connectivity and OPC/driver strategy | Need | Confirm driver support for existing Allen-Bradley PLCs and clarify whether native Ignition drivers or OPC servers will be used, including where those components are hosted. | RSLinx and FactoryTalk Linx providing PLC connectivity; OPC topology implicit in current system design. | Ignition native EtherNet/IP driver and/or OPC servers documented, with clear ownership of where drivers/OPC servers run and how PLC connections are managed. | Not Started | FBCO & One Shot | Ensure alignment with PLC vendor recommendations and corporate standards for OPC/driver deployment.
11 | Screens/HMI | Equipment/tag relabeling and graphics cleanup (equipment, evaporators, NH3 sensors, decommissioned units) | Need | Update equipment, evaporator, and NH3 sensor labeling/tag naming to reflect current function and the current P&ID structure, including clear identification of NH3 alarm sensors, and remove decommissioned equipment still depicted on HMI graphics. | Equipment labeled per original build function; evaporator tags use outdated naming; no structure exists to indicate NH3 alarm sensors; decommissioned evaporators still have associated HMI graphics on the Plant Overview screen -- labeling and graphics are mislabeled and inconsistent overall. | Equipment, evaporator, and NH3 sensor labels/tags renamed to reflect current function, aligned to the current P&ID structure and the plant-wide tag naming standard (ID 28); only physical, in-service equipment shall have an associated graphic. | Not Started | FBCO & One Shot | Verify equipment status with maintenance records before removing graphics. Coordinate closely with tag naming standard (ID 28).
12 | Hardware | Replace temperature probes | Want | Replace Opto22 ICTD temperature probes. | ICTD temperature probes input directly to the PLC card. | Replace ICTD probes with RTDs (or another suitable sensor) and modify PLC code accordingly. | Not Started | FBCO | Confirm RTD compatibility with existing PLC I/O cards before ordering hardware.
13 | Integration | Digitize manual logs, forms, and PSM documentation into Ignition | Need | Provide access to daily rounds, P&ID forms, and PSM program tracking/log spreadsheets for completion and centralized management through Ignition. | Daily rounds and P&ID forms are paper-based and manually transcribed to Excel; PSM program logs are maintained as multiple separate spreadsheets across different areas. | All identified forms and logs (daily rounds, P&ID forms, PSM tracking/logs) consolidated into Ignition for real-time data capture and centralized access, based on a master copy structure. | Not Started | FBCO & One Shot | Confirmed by Refrigeration Operator that these are the same forms, plus additional scope not yet itemized -- follow up to identify the remaining forms/logs referenced.
14 | Integration | Evaporator fan start timer bypass | Want | Provide an override for the evaporator start timer. | Operators must wait 2-5 minutes to start evaporators within the HMI. | Integrate an override capability into evaporator control. | Not Started | FBCO | Confirm safety rationale for existing delay before removing/bypassing it.
18 | Integration | Add TON/TOFF timer function for evaporator start | Need | Provide an adjustable timer function for evaporator fan start/stop to prevent short-cycling caused by the temperature probe. | Current control uses only a deadband, which is not effective in preventing short-cycle stoppage. | Retain the deadband and add an adjustable timer for start/stop control. | Not Started | FBCO | Confirm timer values with refrigeration engineer to avoid compressor short-cycling.
19 | Integration | Hand-Off-Auto (HOA) switch for NH3 pumps | Need | Add a Hand-Off-Auto (HOA) function to NH3 pumps in the HMI; currently the pump will not run without the compressor running. | Pump cannot run independently of the compressor. | Add HOA control for NH3 pumps in the HMI. | Not Started | FBCO | Confirm interlock logic with compressor status is preserved in new HOA design.
20 | Alarming | Alarm disregard function and alarm management standard | Need | Establish alarm management practices beyond individual alarm points -- including acceptable alarm rates, standing/nuisance alarm handling, and shelving/suppression rules -- and add a true disregard function so operators can take needed control actions (e.g., running NH3 pumps) without certain alarms disabling all associated controls. | No formal alarm management standard exists; certain alarms (e.g., a Hi-Hi level alarm in vessels) currently disable all associated controls, preventing operators from remedying the condition. | Documented alarm philosophy (aligned to ISA-18.2 concepts) applied across Ignition alarm configuration, including a true disregard function for alarms that require an operator control action to resolve. | Pending Input | FBCO | Requires PSM review -- disregard functions on safety alarms need documented justification. Ask operator to walk through a bad alarm day -- noise vs. real alarms.
22 | Historian | Improved trending interface | Need | Provide an intuitive trending interface for users. | The current trending user interface is difficult to navigate. | Provide an easily navigable historian trending interface. | Not Started | FBCO & One Shot | Gather specific user complaints about current UI to guide design.
25 | Integration | Integrate NH3 PPM levels into alarm screens | Need | Display parts-per-million (PPM) levels from NH3 sensors to improve safety for refrigeration responders. | No indication of PPM level is currently available. | Provide continuous PPM level monitoring. | Not Started | FBCO | Confirm PPM sensor data is available via existing PLC/OPC tags.
26 | Architecture | Gateway topology, environments, and redundancy | Need | Define dev/prod gateway model, backup/restore procedures, network segmentation, and redundant server failover for high availability of the 24/7 production line. | Single FactoryTalk SE environment, limited separation between development and production, backup/restore handled ad-hoc, and no redundant server pair. | Documented Ignition architecture with separate dev/prod gateways as appropriate, defined backup/restore procedures, network segmentation (controls network, DMZ, corporate) consistent with IT standards, and redundant gateways (e.g., one located locally at RCP and one networked at BH). | Not Started | FBCO | Coordinate with corporate IT and Ignition integrator; confirm network path and failover time requirements between RCP and BH gateways. Another network card will need to be added to the PLC in RCP to support the PLC-managed LAN for gateway/redundancy connectivity.
28 | Data Model | Tag naming, hierarchy standard, and equipment UDTs | Need | Establish plant-wide tag naming and folder hierarchy aligned to equipment and P&ID structure, and define reusable UDTs for major equipment classes (compressors, vessels, evaporators, NH3 sensors) with consistent properties and alarm points. | Legacy tag naming with mixed conventions; equipment and P&IDs not consistently reflected in tag structure; equipment represented with individual tags and ad-hoc groupings, with limited reuse of structured tag definitions. | Standardized tag naming convention and folder hierarchy (e.g., Area > System > Equipment > Function) documented and applied in Ignition, implemented via UDTs for compressors, vessels, evaporators, NH3 sensors, and fans with standardized properties and states. | Not Started | FBCO & One Shot | Use existing P&IDs and equipment lists as the basis for naming; coordinate changes with operators and PSM. Tie to alarm rationalization work.
30 | Compliance/PSM | Alarm rationalization and instructions | Need | Map alarm priorities, messages, and operator instructions into Ignition consistent with PSM and safety requirements. | Alarms configured in FactoryTalk with varying message formats and limited embedded instructions. | Rationalized alarm set with clear priorities, standardized messages, and embedded 'what to do' instructions within Ignition alarm views. | Not Started | FBCO | Use existing PSM procedures and incident learnings to define alarm messages and response guidance.
31 | Compliance/PSM | Audit trail, setpoint change tracking, and MOC visibility | Need | Provide traceable, searchable history of changes to safety-critical tags, alarms, and setpoints -- including who made the change, when, and why -- tied to MOC where applicable. | No setpoint change tracking exists; limited or no visibility into who changed safety-critical values and why. | Ignition-based audit trail showing user, time, and change for safety-critical items and setpoints, searchable, with references to MOC IDs or change records where applicable. | Not Started | FBCO | Cross-reference change management workflow (ID 32).
32 | Operations Support | Change management workflow | Need | Define how HMI screens, tags, and alarms are requested, approved, implemented, and documented. | Informal change process for HMI and controls, documentation scattered across emails and spreadsheets. | Documented change workflow for Ignition projects and tag/alarm modifications, including roles, approvals, and required documentation. | Not Started | FBCO | Align with site CMMS and PSM processes so controls changes follow the same discipline as mechanical changes.
33 | Operations Support | Testing and commissioning plan | Need | Create structured FAT/SAT/field test steps for the Ignition migration, focusing on alarms, NH3 systems, and critical controls. | Testing performed ad-hoc during previous controls changes, limited formal test scripts. | Written test plan covering gateway functions, HMI screens, alarms, historian, and refrigeration control scenarios, executed and signed off before cutover. | Not Started | FBCO | Use typical operating and emergency scenarios (e.g., NH3 leak, HiHi level, pump-out) as the basis for test cases.
34 | Safety/Interlocks | Safety interlock and ESD logic | Need | Determine whether emergency shutdown (ESD) and safety interlock logic runs on a separate safety PLC or shares the same processor as the HMI/control system. | Safety interlock logic runs through Allen-Bradley 440-C-CR30 safety relays (PSRs). | Documented safety architecture with clear separation (or justified integration) between safety and process control in Ignition. | Not Started | FBCO | Confirmed by Refrigeration Operator. Requires connection to the PLC-managed LAN.
35 | Compliance/PSM | Refrigerant charge/inventory tracking | Need | Determine whether total NH3 charge/inventory is tracked today and how it should be represented or logged in Ignition for PSM/RMP compliance. | Current NH3 inventory needs to be recalculated; a tracking method has not yet been developed. | NH3 inventory tracking method documented and, if applicable, integrated into Ignition. | Not Started | FBCO | Ask operator whether this is tracked manually, in a separate system, or not tracked at all.
37 | Integration | Compressor sequencing/staging | Need | Clarify how compressor lead-lag sequencing, capacity control, and oil management are currently handled and whether logic needs to be recreated or improved in Ignition. | Compressor sequencing is managed through SICK Quantum control panels. | Compressor sequencing logic documented and implemented/replicated in Ignition. | Not Started | FBCO | Priority discussion topic for Refrigeration Operator meeting.
38 | Integration | Defrost scheduling and sequencing | Need | Determine current defrost scheduling/sequencing logic for evaporators and whether manual workarounds exist. | Defrost control mechanisms are already functioning well in FactoryTalk; logic needs to be documented for the Ignition team. | Defrost logic documented and implemented in Ignition, with scheduling visible/adjustable in the HMI. | Not Started | FBCO | Ask about manual overrides currently used during defrost.
39 | Integration | Pump-out and liquid-level handling | Need | Clarify pump-out sequences and liquid-level handling beyond the existing HiHi alarm, including any manual workarounds operators rely on. | Partial coverage via HiHi level alarm (see ID 20); broader pump-out process not yet documented. | Documented pump-out sequence with appropriate HMI control and alarming in Ignition. | Pending Input | FBCO | Ask operator for manual workarounds tied to pump-out or liquid level.
40 | Compliance/PSM | Fire & gas system integration | Need | Determine whether the fire & gas detection network (horns, strobes, mustering) needs any HMI/Ignition integration beyond displaying PPM levels. | PPM display only (see ID 25); broader fire & gas system integration not yet scoped. | Fire & gas system integration requirements documented, with Ignition scope defined if applicable. | Pending Input | FBCO | This decision lies with local and corporate stakeholders; limited impact on the main scope of this project.
42 | Integration | Third-party system integration (CMMS, corporate historian, etc.) | Want | Identify any systems operators currently re-key data into manually (e.g., CMMS/work orders, corporate historian) that could integrate directly with Ignition. | No third-party integration exists in the current deployment. | Direct integration (or defined data path) between Ignition and identified third-party systems. | Pending Input | FBCO | Ask operator what they currently re-key by hand into other systems.
44 | Alarming | After-hours/on-call alarm notification | Need | Determine whether critical alarm notifications (NH3, Hi-Hi level, ESD) to on-call personnel via text or call should be migrated from the Fire Panel/Emergency 24 monitoring service into Ignition. | Fire alarm panel managed via an Emergency 24 monitoring service. | Critical alarm notification (SMS/email/voice) to on-call staff configured in Ignition. | Pending Input | FBCO | Likely the single biggest ask on an ammonia site — prioritize this question with the operator. Decision-maker: Greg Rogers.
45 | Integration | Head pressure/condenser fan control | Need | Clarify how condenser fan staging and head pressure control are currently handled and whether logic needs to be recreated or improved in Ignition. | To be confirmed with Refrigeration Operator. | Condenser fan/head pressure control logic documented and implemented/replicated in Ignition. | Pending Input | FBCO | Ask operator about seasonal/ambient-driven adjustments to head pressure setpoints.
46 | Data Model | Refrigeration system type (confirmed) | Need | Confirmed pumped liquid overfeed system: NH3 liquid is pumped from the High Temp Recirculator to evaporators via a common header, saturated gas returns to the Recirculator, compressors discharge to a water-cooled condenser, and liquid returns via a Thermosyphon vessel to a High Pressure Receiver. | System type documented; see Description. | Recirculator, Thermosyphon, and High Pressure Receiver represented as distinct equipment classes in the Ignition tag/UDT structure (ID 29). | Complete | FBCO | Confirmed by Refrigeration Operator. Open follow-ups: confirm condenser type (evaporative vs. shell-and-tube with cooling tower) for ID 45; confirm whether a Low Temp Recirculator also exists (two-stage system) for ID 28.
47 | Data Model | Validate P&IDs against field conditions | Need | Verify existing P&IDs reflect actual field conditions before using them as the basis for tag naming and hierarchy work. | Decommissioned equipment found still depicted in HMI graphics (see ID 17), suggesting possible P&ID/field drift. | P&IDs field-verified and corrected where needed prior to tag naming/hierarchy standardization (ID 28). | Not Started | FBCO | An annual P&ID review must be completed and updated prior to mobilization -- at minimum a full equipment listing, with fully updated drawings and listings as the goal.
48 | Networking | OT endpoint protection and patch management | Need | Define antivirus/endpoint protection, patch management, and remote vendor access security policies for Ignition gateways and related OT devices. | No documented OT endpoint protection or patch management policy. | Documented OT security policy covering endpoint protection, patching cadence, and secure remote vendor access. | Pending Input | FBCO | Coordinate with corporate IT/OT security standards; align with gateway topology work (ID 26).
49 | Networking | Time synchronization (NTP) across gateways | Want | Ensure consistent timestamps across Ignition gateways, historian, and alarm logs via network time synchronization. | Time synchronization method not currently documented. | NTP (or equivalent) configured across all Ignition gateways and related systems. | Pending Input | FBCO | Easy to overlook, but important for alarm/historian timestamp accuracy.
50 | Networking | Ignition project version control | Want | Establish version control (e.g., Git integration) for Ignition project files, separate from gateway configuration backup/restore. | No version control currently in place for controls project files. | Ignition projects tracked in a version control system with change history. | Pending Input | FBCO & One Shot | Distinct from gateway backup/restore already covered in ID 26.
51
52
53
54
55
56
57
58
59
60
61
62

## Legend & Instructions
How to use this tracker
1. | Add one row per requirement on the 'Wants & Needs' tab. Row 5 (with grey italic note) is an example — edit or delete it.
2. | Priority: Need = must-have for go-live · Want = important but not a blocker · Nice to Have = bonus if time/budget allow.
3. | Category, Priority, and Status columns have dropdown menus — click the cell to select a value.
4. | Use 'Current State' and 'Target State' to document what exists today in FactoryTalk vs. the planned Ignition equivalent.
5. | Update the Status column as work progresses to keep the whole team aligned.
Priority color key:
Need
Want
Nice to Have